## Sheet1
TIGERFLOW Booster Sizing Worksheet
Job Name:
Customer:
I. Pressure Required:
| A. Pressure required at highest fixture | [6 empty] | 30 | PSI
(Estimate 30-40 PSIG +/-, or specifed requirement)
| B. Static head |  |  | (building height = |  | 120 | ft) | 51.9481 | PSI
| C. Piping and system friction loss |  |  |  | (10% of static head) |  |  | 5.1948 | PSI
| D. Required system processing |  |  |  | (A + B + C) |  |  | 87.1429 | PSI
| E. Subtract minimum suction pressure at pump station | [6 empty] | 30 | PSI
(Minimum suction pressure at street minus pressure
drop through backflow prevention and / or water meter)
| F. Subtotal |  | (D + E) |  |  |  |  | 57.1429 | PSI
| G. Internal booster station loss | [6 empty] | 5 | PSI
| H. Total pump boost (differential) pressure required (F + G) | [6 empty] | 62.1429 | PSI
| I. Convert pump boost PSI to TDH |  |  |  |  | (PSI x 2.31 = |  | 143.55 | ft, TDH)
II. Fixture Unit Table:
|  | Fixture |  |  | Use | Fixture Units | No. of Fixtures | Total
|  | Bathroom group flush valve |  |  | Public | 8 |  | 0
|  | Bathroom group flush tank |  |  | Private | 6 |  | 0
|  | Lavatory |  |  | Public | 2 |  | 0
|  | Urinal - flush valve |  |  | Public | 5 |  | 0
|  | Water closet - flush valve |  |  | Public | 10 |  | 0
|  | Water closet - flush valve |  |  | Private | 5 |  | 0
|  | Bathtub - public |  |  | Public | 4 |  | 0
|  | Bathtub - private |  |  | Private | 2 |  | 0
|  | Bathtub - immersion |  |  | Public | 20 |  | 0
|  | Shower (standard) |  |  | Public | 4 |  | 0
|  | Sink - kitchen |  |  | Public | 4 |  | 0
|  | Sink - kitchen |  |  | Private | 2 |  | 0
|  | Sink - services |  |  | Public | 3 |  | 0
|  | Garbage disposal |  |  | Public | 3 |  | 0
|  | Garbage disposal |  |  | Private | 2 |  | 0
|  | Dishwasher |  |  | Public | 6 |  | 0
|  | Dishwasher |  |  | Private | 2 |  | 0
|  | Washing machine |  |  | Public | 4 |  | 0
|  | Washing machine |  |  | Private | 2 |  | 0
|  | Ice machine |  |  | Public | 1 |  | 0
|  | Steam tables |  |  | Public | 1 |  | 0
|  | Hose connection - 3/4" |  |  | Public | 6 |  | 0
[5 empty] | Total Fixture Units |  |  | 0
Typical System GPM
|  | Fixture Units | Apts / Office | Hotel / Motel | Hospital / School / Prison |  |  |  |  | Apts / Office | Hotel / Motel | Hospital / School / Prison
|  | 0 | 0 | 0 | 100
|  | 100 | 70 | 80 | 100
|  | 300 | 80 | 90 | 100 | 0 | 0 | 0 |  | 0.05 | 0.05 | 0
|  | 600 | 100 | 120 | 130 | 0 | 0 | 0 |  | 0.066667 | 0.1 | 0.1
|  | 900 | 120 | 125 | 140 | 0 | 0 | 0 |  | 0.066667 | 0.016667 | 0.033333
|  | 1200 | 140 | 150 | 160 | 0 | 0 | 0 |  | 0.066667 | 0.083333 | 0.066667
|  | 1500 | 150 | 170 | 190 | 0 | 0 | 0 |  | 0.033333 | 0.066667 | 0.1
|  | 1650 | 170 | 180 | 200 | 0 | 0 | 0 |  | 0.13333 | 0.066667 | 0.066667
|  | 1750 | 180 | 190 | 210 | 0 | 0 | 0 |  | 0.1 | 0.1 | 0.1
|  | 2000 | 190 | 200 | 220 | 0 | 0 | 0 |  | 0.04 | 0.04 | 0.04
|  | 2200 | 210 | 220 | 230 | 0 | 0 | 0 |  | 0.1 | 0.1 | 0.05
|  | 2500 | 220 | 240 | 260 | 0 | 0 | 0 |  | 0.033333 | 0.066667 | 0.1
|  | 3000 | 250 | 275 | 300 | 0 | 0 | 0 |  | 0.06 | 0.07 | 0.08
|  | 4000 | 300 | 350 | 375 | 0 | 0 | 0 |  | 0.05 | 0.075 | 0.075
|  | 5000 | 350 | 400 | 450 | 0 | 0 | 0 |  | 0.05 | 0.05 | 0.075
|  | 6000 | 400 | 450 | 500 | 0 | 0 | 0 |  | 0.05 | 0.05 | 0.05
|  | 7000 | 450 | 500 | 550 | 0 | 0 | 0 |  | 0.05 | 0.05 | 0.05
|  | 8000 | 500 | 550 | 600 | 0 | 0 | 0 |  | 0.05 | 0.05 | 0.05
|  | 10000 | 550 | 600 | 650 | 0 | 0 | 0 |  | 0.025 | 0.025 | 0.025
IV. Total System Demand (GPM):
[6 empty] | Apts / Office | Hotel / Motel | Hospital / School / Prison
| A. System demand (GPM) |  |  | (Total Chart III) |  | 0 | 0 | 100
| B. Special duty demands (GPM) |  |  |  |  | 0 | 0 | 0
(Cooling tower makeup, etc.)
Flow
| C. Total systems demand |  |  |  |  | 0 | 0 | 100 |  | 100
Duplex: (0 - 300 GPM) Apts / Office | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  |  |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est)
50-50 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.5 | 0.5 | 0
33-67 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.33 | 0.67
65-65 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.65 | 0.65
100-100 |  |  | 0 | 0 | 0 | 0 |  |  |  | 1 | 1
Duplex: (0 - 300 GPM) Hotel / Motel | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  |  |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est)
50-50 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.5 | 0.5 | 0
33-67 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.33 | 0.67
65-65 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.65 | 0.65
100-100 |  |  | 0 | 0 | 0 | 0 |  |  |  | 1 | 1
Duplex: (0 - 300 GPM) Hospital / School / Prison | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  |  |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est)
50-50 |  |  | 50 | 2.3925 | 50 | 2.3925 |  |  |  | 0.5 | 0.5 | 0
33-67 |  |  | 33.33 | 1.5948 | 66.66 | 3.1897 |  |  |  | 0.33 | 0.67
65-65 |  |  | 65 | 3.1102 | 65 | 3.1102 |  |  |  | 0.65 | 0.65
100-100 |  |  | 100 | 4.785 | 100 | 4.785 |  |  |  | 1 | 1
Duplex: (0 - 300 GPM) Apts / Office | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  | Pump #3 |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est) | GPM | HP (est)
10-50-50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.5 | 0.5 | 0
20-40-40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.33 | 0.67
33-33-33 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.65 | 0.65
50-50-50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1
Duplex: (0 - 300 GPM) Hotel / Motel | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  | Pump #3 |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est) | GPM | HP (est)
10-50-50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.5 | 0.5 | 0
20-40-40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.33 | 0.67
33-33-33 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.65 | 0.65
50-50-50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1
Duplex: (0 - 300 GPM) Hospital / School / Prison | [9 empty] | Density | Pump Eff | gpm2cfs | lbfts2hp
143.55 |  | ft, head | Pump #1 |  | Pump #2 |  | Pump #3 |  |  | 64.1 | 0.65 | 0.002228 | 0.0018182
% of System GPM |  |  | GPM | HP (est) | GPM | HP (est) | GPM | HP (est)
10-50-50 |  |  | 10 | 0.4785 | 50 | 2.3925 | 50 | 2.3925 |  | 0.5 | 0.5 | 0
20-40-40 |  |  | 20 | 0.957 | 40 | 1.914 | 40 | 1.914 |  | 0.33 | 0.67
33-33-33 |  |  | 33.33 | 1.5948 | 33.33 | 1.5948 | 33.33 | 1.5948 |  | 0.65 | 0.65
50-50-50 |  |  | 50 | 2.3925 | 50 | 2.3925 | 50 | 2.3925 |  | 1 | 1
VI. Maximum Flow Rate (GPM) per Header Size:
|  |  | Size (inches) | Flow (GPM)
|  |  | 3 | 300
|  |  | 4 | 600
|  |  | 6 | 1000
|  |  | 8 | 1800
|  |  | 10 | 2800
|  | Minimum header size for this job = |  |  |  | 3 | Inch
TIGERFLOW Systems, Inc.
4034 Mint Way
Dallas, Texas 75237
214-337-8780
800-783-6756
214-333-2742 FAX
www.tigerflow.com