## TEXAN DCP SCHEDULE
DOMESTIC WATER BOOSTER PUMP SCHEDULE
TAG | LOCATION | SERVICE | MANUFACTURER | MODEL | SYSTEM FLOW RATE | DISCHARGE PRESSURE | SUCTION PRESSURE | NUMBER OF PUMPS | CONNECTION TYPE | APPROX WEIGHT | POWER AVAILABLE |  |  | PUMP 1: | PUMP 2: | PUMP 3: | PUMP 4: | PUMP 5: | SCCR | NOTES
[5 empty] | (GPM) | (PSI) | (PSI) | (QTY) | FLANGED / GROOVED | (LBS) | (V) | (PH) | (HZ) | (HP) | (HP) | (HP) | (HP) | (HP) | (KA)
BP-1 | EXAMPLE | DOMESTIC | TIGERFLOW TEXAN DCP | VMS-4000-V-TDCP | 200 | 250 | 15-40 | 3 | FLANGED | 1000 | 460 | 3 | 60 | 7.5 | 7.5 | 5 | NA | NA | 100 | ALL
NOTES: | (THIS COLUMN IS FOR STANDARD COMPONENTS, DO NOT EDIT) | [8 empty] | (LBS): NOTES CONTINUED:; (PH): This column is for options available. Add or subtract here
1 | BOOSTER SHALL UTILIZE CONTROLLER EMBEDDED IN VFDS. 3RD PARTY PLC LOGIC CONTROL IS NOT ACCEPTABLE | [8 empty] | (LBS): 11; (V): BOOSTER SHALL HAVE 316 STAINLESS STEEL HEADERS
2 | VFDS SHALL BE ABB ACH580 DRIVES, WITH CIRCUIT BREAKERS | [8 empty] | (LBS): 12; (V): BOOSTER SHALL HAVE VIBRATION ISOLATION PADS
3 | VFDS SHALL HAVE BTL LISTED BACNET MS/TP, AND INCLUDE MODBUS AND N2 CAPABILITIES. | [8 empty] | (LBS): 13; (V): BOOSTER SHALL HAVE SURGE SUPPRESSOR
4 | VFD'S SHALL HAVE FLUX OPTIMIZATION / ENERGEGY OPTIMIZATION | [8 empty] | (LBS): 14; (V): BOOSTER SHALL HAVE FLOW METER (MODEL)
5 | VFD'S SHALL HAVE 5% IMPEDENCE FOR HARMONIC MITIGATION AND ELECTRICAL PROTECTIONS | [8 empty] | (LBS): 15; (V): BOOSTER SHALL HAVE CALCULATED FLOW
6 | VFD'S SHALL HAVE BLUETOOH PROGRAMMING SET UP AND MAINTENANCE CAPABILITIES | [8 empty] | (LBS): 16; (V): BOOSTER SHALL HAVE EVERACTIVE VIBRATION METERS
7 | VFDS SHALL HAVE INTERNAL EMI/RFI FILTER PER IEC 61800-3. | [8 empty] | (LBS): 17; (V): BOOSTER SHALL HAVE WARRANTY - 5 YEARS
8 | BOOSTER SHALL HAVE SINGLE POINT POWER CONNECTION FOR ENTIRE BOOSTER SKID | [8 empty] | (LBS): 18
9 | BOOSTER SHALL HAVE INDEPENDENT SUCTION AND DISCHARGER PRESSURE TRANSDUCERS PER PUMP | [8 empty] | (LBS): 19
10 | BOOSTER SHALL BE PROVIDED BY TEXAS AIR SYSTEMS. CONTACT DANIEL MERKEL. 817.838.7400